## Technologies
Basic Info |  |  | Description & Applicability | [6 empty] | Building Decarbonization Attributes | [7 empty] | Technology Review |  |  |  | Company Information |  |  |  |  | Market Data | [11 empty] | Installation Data | Additional References | Additional Info / Notes
Company Name | Product Name | Website / Reference | Technology Focus Area | Building System | Subsystem Type | Any Critical Prerequisite Condition | Technology Type | Relevant Building Type | Basic Description | Climate Impact Potential (Building Level) | Future Climate Impact Potential (Building Level) | Climate Impact Potential (State Level) | Future Climate Impact Potential (State Level) | Climate Impact Type | Climate Impact Description | Cost Effectiveness Potential | Cost Effectiveness Description | Technology Development Category | Technology Readiness Level | Risk Category | Key Technical Risks | HQ Location | Affliated Locations In US | Growth Phase | Company Size | Contact Information @ Company | US Total Addressable Market | Current US Market Size | US Market Penetration | NY Total Addressable Market | NY Current Market Size | NY Market Penetration | Global Total Addressable Market | Global Current Market Size | Global Market Penetration | Reason for Widespread/Limited Adoptions | Enter NY Threshold for Sales Office | Enter NY Threshold for Manufacturing | Relevant Trigger Points
Vilisto | Ovis | Website | Energy Distribution | Heating | Steam Radiators | - | Radiator Control | All | Self-learning radiator controller w/ occupancy, comfort and weather consideration. | 6 - 10% | 6 - 10% | 0.57% | 0.78% | Efficiency & Demand Flexibility | Uses local weather, occupancy and room climate to regulate radiator valves. Allows for pre-heating (demand flexibility) and prevents excess heating (efficiency). Reducing energy consumption from steam systems. | Medium-term Payback | As algorithms are improved, improved controls could result in higher heating savings and faster paybacks. | Global Best Practice | N/A | Low | No Substantial Risk. | Hamburg, Germany | N/A | Startup/Launch | 11-50 Employees | info@vilisto.de 040 3346 812 00 |  | $0/yr | 0% |  | $0/yr | 0% |  |  |  | Adoption becoming more commonplace due to better performing wireless data transmission and improved controls. |  |  | No Trigger Required
VoltServer | VoltServer | Website | Energy Distribution | Electrical | Power Distribution | c | Digital Electricity | All | Equipment to transmit/receive patented 'Digital Electricity': Touch-safe pulsed high-voltage DC power combined with data which is supplied via 'packets'. | < 1 % | < 1 % | 0% | 0% | Enabler | Does not reduce GHG emissions directly. VoltServer's 'Digital Electricity' technology enables the delivery and monitoring of "electricity packets" which could enhance microgrid reliability, especially in tall buildings with lengthy cable runs. | Medium-term Payback | Coupling of power/communication in a single wire allows for cost-effective deployment with less copper and less conduit. | Emerging | N/A | High | Implementation of a new form of electrical distribution where few have the technical expertise. | East Greenwich, RI, USA | N/A | Growth | 11-50 Employees | (888) 622-8658 contact@voltserver.com | [9 empty] | Skepticism about a new form of electrical distribution. |  |  | Electrical System Upgrade |  | 1. Presentation on Digital Electricity: https://vimeo.com/172469008 2. Explanation: https://www.belden.com/blog/smart-building/digital-electricity-5-things-you-need-to-know
Belden | Digital Electricity Cables | Website | Energy Distribution | Electrical | Power Distribution | Cabling is only compatible with 'Digital Electric' systems - requires VoltServer's transmitters and receivers. | Digital Electricity | All | Specialized 'Digital Electricity' copper/fiber hybrid cables for power and data. | < 1 % | < 1 % | 0% | 0% | Enabler | Does not reduce GHG emissions directly. | Short-term Payback | Low-cost, cabling from established manufacturer. | US Best Practice | N/A | Low | No Substantial Risk. | St. Louis, Missouri, USA | N/A | Established | 200+ Employees | (800) 235-2361 -- Sales | [9 empty] | Cable is reliant on the adoption of 'Digital Electricity' (see VoltServer). |  |  | Electrical System Upgrade
Solid Air International | GKP Climate Ceiling | Website | Energy Distribution | Heating, Cooling | Hydronic Systems | - | Radiant Ceiling Panel | Commercial | Plasterboard/Stucco-concealed radiant heating and cooling panels. | 6 - 10% | 11 - 20% | 1.6% | 1.94% | Efficiency | Reduces distribution energy and enables low temp heating / higher temperature cooling | Medium-term Payback | Potential to be more cost effective than traditional radiant panels due to multi-function and ease of installation | Global Best Practice | N/A | Medium | In cooling systems there is risk of condensation buildup if dew-point isn't properly monitored. | Westerbroek, Groningen, Netherlands | N/A | Growth | 11-50 Employees | +31 598 36 12 21 mail@solid-air.com |  | $0/yr | 0% |  | $0/yr | 0% |  |  |  | Relatively widespread in UK and Europe due to efficiency, not established in US and faces barrier of humidity concerns and lower prevalence of hydronic systems in US |  |  | Renovation of Tenant Space
ClimaDomo | Ceiling Modules | Website | Energy Distribution | Heating, Cooling | Hydronic Systems | - | Radiant Ceiling Panel, Radiant Wall Panel | All | Capillary tube mats integrated in drywall / plasterboard for radiant cooling/heating. | 6 - 10% | 11 - 20% | 1.6% | 1.94% | Efficiency | Reduces distribution energy and enables low temp heating / higher temperature cooling | Medium-term Payback | Potential to be more cost effective than traditional radiant panels due to multi-function and ease of installation | Global Best Practice | N/A | Medium | In cooling systems there is risk of condensation buildup if dew-point isn't properly monitored. | Kölleda, Thuringia, Germany | N/A | Established | 11-50 Employees | (+49) (0) 3635 60 26 90 info@climadomo.de |  | $0/yr | 0% |  | $0/yr | 0% |  |  |  | Relatively widespread in Europe, faces similar barriers to radiant cooling in US (humidity control concerns), requires disruptive retrofit |  |  | Renovation of Tenant Space
Legend Power | SmartGATE | Website | Energy Distribution | Electrical | Power Distribution | - | Voltage Power Management | All | Power management platform and in-built auto-transformer for voltage/phase regulation from a utility source | 1 - 5% | 1 - 5% | 0.33% | 0.24% | Efficiency | Corrects power quality issues from the electric utility which enhances the energy efficiency of downstream equipment. | Medium-term Payback | As algorithms are improved, power modulation could become faster and more accurate - resulting in more efficiencies and faster paybacks. | US Best Practice | N/A | Low | No Substantial Risk. | Vancouver, British Columbia, Canada | N/A | Established | 51-200 Employees | (866) 772-8797 info@legendpower.com | [9 empty] | Power quality management is well adopted by industrial customers who need consistent power. Hasn't been a lower-cost product in the market for commercial/residential. |  |  | Electrical System Upgrade |  | 1. Sales -- https://www.globenewswire.com/news-release/2020/02/13/1984438/0/en/Legend-Power-Closes-over-500-000-of-SmartGATE-Sales.html 2. Quarterly Reports - https://legendpower.com/wp-content/uploads/2020/09/LPS-MDA-Jun-30-2020-FINAL.pdf
ThermaXX | Smart Jackets | Website | Energy Distribution | Heating, Cooling, DHW | Hydronic Distribution | - | Piping Insulation | All | Custom fabricated, removable insulation covers w/ temperature sensors for valves, strainers, large steam traps, and odd-shaped piping which are typically left uninsulated. | < 1 % | < 1 % | 0.07% | 0.1% | Efficiency | Increases the efficiency of a building's heating system by preventing heat loss. | Short-term Payback | Low-cost, not disruptive. | US Best Practice | N/A | Low | No Substantial Risk. | West Haven, CT USA | N/A | Growth | 11-50 Employees | (203) 672-1021 Fax: (203) 437-6955 info@thermaxxjackets.com | [9 empty] | Emerging Technology filling a niche market. |  |  | No Trigger Required | 1 -- https://be-exchange.org/innovative-steam-solutions-for-new-york-city/ | https://marketplace.city/c/thermaxx/
Tsinghua University and Brown University | HFE Additive for Turbulent Heat Exchangers | Website | Energy Distribution | Heating, Cooling | Hydronic Systems | - | Heat Transfer Enhancement | All | Heat transfer additive (readily available organic solvent-hydrofluoroether) for turbulent heat exchangers that improves heat exchange by up to 500% | 11 - 20% | 21 - 30% | 1.56% | 1.94% | Efficiency | Increases the effectiveness of heat transfer. High uncertainty of savings in real world application | Long-term Payback | Cost effectiveness of HFE additive is unknown | Emerging | 3 | low | Unknown | Tsinghua U (China) | Brown University | pre-startup | 1-10 Employees | - |  | $0/yr | 0% |  | $0/yr | 0% |  | $0/yr | 0% | early phases of research, i.e. not on the market |  |  | No Trigger Required |  | Research is focused on HFE, which in non-corrosive, non-flammable and ozone-friendly. Only used in vertical turbulent heat exchangers.
University of Kerala | Nano-refrigerants |  | Energy Distribution | Heating, Cooling | Refrigerant | Refrigerant replacement | Nanorefrigerant | All | Suspensions of solid submicron- and nanometer-sized particles in fluids are called nanofluids. Nanorefrigerants are nanofluids in refrigerants. R134a + CuO/Polyalkylene glycol boosts heat transfer ability of low GWP refrigerants, like R-134A, research shows increase of COP by 7-8% | < 1 % | < 1 % | 0.04% | 0.03% | Efficiency | Very focused optimization of refrigerant loops, which have limited application | Medium-term Payback | Copper additives should be relatively cost effective | Emerging | 1 | high | Unknown commercial viability | Kerala, India |  | pre-startup | 1-10 Employees | University of Kerala (India) - Prof Sanukrishna |  | $0/yr | 0% |  | $0/yr | 0% |  | $0/yr | 0% | Variability in nanofluid products and they have not been produced to scale |  |  | No Trigger Required |  | Make low GWP more effective and comparable to current market options.
University of Waikato | Aluminum nanofluids | Website | Energy Distribution | Heating, Cooling | Hydronic Systems | - | Heat Transfer Fluids | All | Suspensions of solid submicron- and nanometer-sized particles in fluids are called nanofluids. These are water based applications have proven to increased heat transfer of 10-20%, but are not seen widely in industry applications yet. | 6 - 10% | 6 - 10% | 0.57% | 0.73% | Efficiency | Increases the effectiveness of heat transfer | Medium-term Payback | aluminum additives should be relatively cost effective | Emerging | 5 | high | lots of unknowns on commercial viability | University of Waikato, Hamilton, New Zealand |  | pre-startup | 1-10 Employees | ffdkd@uaf.edu |  | $0/yr | 0% |  | $0/yr | 0% |  | $0/yr | 0% | Variability in nanofluid products and they have not been produced to scale |  |  | No Trigger Required |  | commercial viability is unknown but the research shows promising results. Compared to silicon, and copper options, aluminum shows best performance. The tradeoff between higher viscosity and decreased flow rate requirements are unknown in terms of their impact on pumping power (different systems would have different impacts).
Big Ass Fans | Haiku | Website | Energy Distribution | Heating, Cooling | Fans | - | High Volume Low Speed Fan | All | Efficient fan to promote mixing / heating and cooling distribution. | 1 - 5% | 6 - 10% | 0.48% | 1.28% | Efficiency | Encourages mechanical ventilation and saves energy with large lower speed fans that move a lot of air. | Short-term Payback | Low-cost, not disruptive. | US Best Practice | N/A | Low | No Substantial Risk. | Lexington, KY, USA | N/A | Established | 200+ Employees | 2348 Innovation Drive Lexington, KY 40511 877-BIG-FANS or 844-322-5809 | 1754100000 |  |  | 103000000 |  |  | 32500000000 |  |  | Common and efficient technology type |  |  | Renovation of Tenant Space |  | There are several other manufactures of High volume low speed fans
Radiator Labs | The Cozy | Website | Energy Distribution | Heating | Steam Radiators | - | Insulated Radiator Enclosure | Commercial | An insulated enclosure for radiators with thermostatically controlled fan to modulate radiator output | 6 - 10% | 11 - 20% | 0.54% | 1.08% | Demand Flexibility | Reduces energy use by insulating and introducing temperature control to outdated steam radiators | Short-term Payback | Low-cost, not disruptive. | US Best Practice | N/A | Low | There are a multitude of radiator sizes and this requires custom enclosures. | Brooklyn, NY, USA | N/A | Startup/Launch | 1-10 Employees | 63 Flushing Ave Building 292, Suite 409 Brooklyn, NY 11205 646.902.HEAT (4328) | [9 empty] | Emerging technology |  |  | No Trigger Required
Price Industries | Price Linear Passive Beam (PCBL) | Website | Energy Distribution | Cooling | Hydronic Systems | - | Chilled Beam | All | Passive chilled beam that does not require supply air, cools through natural convective movement of air through the coil. | 6 - 10% | 6 - 10% | 0.97% | 1.42% | Efficiency | Reduces distribution energy and enables low temp heating/ temp cooling | Medium-term Payback | Chilled beams allow decoupling of sensible loads from ventilation air and allow for reduced duct sizes and higher ceiling heights. | US Best Practice | N/A | High | Condensation risk | Suwanee, Georgia, USA | All States | Established | 200+ Employees | 2975 Shawnee Ridge Court NW Suwanee, Georgia 30024 (770) 623-8050 info@priceindustries.com | [9 empty] | Energy efficiency and established credibility |  |  | Full Major Building Retrofit
TROX GmbH | SMART BEAM | Website | Energy Distribution | Heating, Cooling | Hydronic Systems | - | Chilled Beam | All | Active chilled beam with air discharge and heat exchanger. Allowing for heating and cooling option. | 11 - 20% | 11 - 20% | 1.84% | 2.61% | Efficiency | Reduces energy use by eliminating excessive fan use. | Medium-term Payback | Chilled beams allow decoupling of sensible loads from ventilation air and allow for reduced duct sizes and higher ceiling heights. | Global Best Practice | N/A | High | Condensation risk | Neukirchen-Vluyn, Germany | Georgia | Established | 51-200 Employees | Heinrich-Trox-Platz D-47504 Neukirchen-Vluyn Tel.: +49 (0)2845 202-0 Fax: +49 (0)2845 202-265 | [9 empty] | Energy efficiency and established credibility |  |  | Full Major Building Retrofit
Lindner | Plafotherm | Website | Energy Distribution | Heating, Cooling | Hydronic Systems | - | Radiant Ceiling Panel | Commercial | Radiant Heating and Cooling Panels | 6 - 10% | 11 - 20% | 1.45% | 2.27% | Efficiency | Reduces distribution energy and enables low temp heating/ temp cooling | Medium-term Payback | Potential to be more cost effective than traditional radiant panels due to multi-function and ease of installation | Global Best Practice | N/A | Low | Requires careful monitoring of dew points and surface temperatures to prevent condensation. | Germany | 5125 South Royal Atlanta Drive, Tucker, GA 30084 | Established | 200+ Employees | usa@Lindner-Group.com +1 770 414 5054 | [9 empty] | Energy efficiency and established credibility |  |  | Renovation of Tenant Space
AIC | JAD Line Heat Ex | Website | Energy Distribution | Heating | Hydronic Heat Exchangers | - | Higher efficiency HX | All | Vertical HX's with concentrically layered, helically corrugated heat exchanger tubes. | 1 - 5% | 1 - 5% | 0.42% | 0.58% | Efficiency | Higher efficiency shell and tube heat exchangers due to helically wrapped corrugated tubes. Reduced leaving condensate water temperatures. | Short-term Payback | Low-cost, not disruptive. | Global Best Practice | N/A | Low | NA | Poland and Canada | N/A | Established | 51-200 Employees | ask@aicheatexchangers.com | [9 empty] | Energy efficiency |  |  | Chiller/Boiler Replacement
Warmboard-R | Warmboard | Website | Energy Distribution | Heating, Cooling | Hydronic Systems | - | Radiant Tubing Manifold | All | Panels that allow for radiant tubing to be installed. Specifically designed for retrofit applications | 6 - 10% | 11 - 20% | 1.5% | 2.03% | Efficiency | Reduces distribution energy and enables low temp heating/ temp cooling | Medium-term Payback | Potential to be more cost effective than traditional radiant panels due to multi-function and ease of installation | US Best Practice | N/A | Low | Requires careful monitoring of dew points and surface temperatures to prevent condensation. | Aptos, California, USA | Aptos, California | Established | 200+ Employees | 8035 Soquel Dr. Ste 41a Aptos, CA 95003 8773385493 | [9 empty] | Energy efficiency and established credibility |  |  | Full Major Building Retrofit
Giacomini | Radiant Panel | Website | Energy Distribution | Heating, Cooling | Hydronic Systems | - | Radiant Tubing Manifold | All | Floor, ceiling, and wall panels allowing for radiant tubing for new construction and expansion | 6 - 10% | 11 - 20% | 1.62% | 1.96% | Efficiency | Reduces distribution energy and enables low temp heating/ temp cooling | Medium-term Payback | Potential to be more cost effective than traditional radiant panels due to multi-function and ease of installation | Global Best Practice | N/A | Low | Requires careful monitoring of dew points and surface temperatures to prevent condensation. | San Maurizio, Italy | N/A | Established | 11-50 Employees | Via Per Alzo, 39 - 28017 San Maurizio d'Opaglio (NO)- Italy +39 0322 923111 info@giacomini.com | [9 empty] | Energy efficiency and established credibility |  |  | Full Major Building Retrofit
ThermOmegaTech | Circuit Solver Valves | Website | Energy Distribution | DHW | DHW Recirculation | Central domestic hot water loop serving multiple zones | Thermostatically regulated valve for DHW loop | Residential | Self actuating thermostatically regulated valve which auto balances DHW recirculation loops, minimizes pumping and heat losses of recirculation system by reducing flow when branches are at temperature | 1 - 5% | 1 - 5% | 0.17% | 0.63% | Demand Flexibility | Reduces heating energy by introducing automatic DHW balancing | Short-term Payback | Low-cost, not disruptive. | US Best Practice | N/A | Low | No Substantial Risk. | Warminster, Pennsylvania, USA | All US | Established | 200+ Employees | 353 Ivyland Road Warminster, PA 18974-2205 8773798258 | [9 empty] | Cost and ease of installation |  |  | Chiller/Boiler Replacement
Therm | Automatic Wireless Radiator Valve | Website | Energy Distribution | Heating | Steam Radiators | - | Radiator Control | All | Thermostatic control on a cycling one-pipe radiator steam system on Heat-timer or similar | 6 - 10% | 11 - 20% | 0.54% | 1.08% | Efficiency & Demand Flexibility | Reduction of waste heat by regulating steam flow in radiators. | Short-term Payback | Low-cost, not disruptive. | Emerging | 7 | Low | No Substantial Risk. | New York, NY, USA | N/A | Pre-startup | 1-10 Employees | experience@hellotherm.com |  | $0/yr | 0% |  | $0/yr | 0% |  | $0/yr | 0% | Easy retrofit option |  |  | No Trigger Required |  | * Note that there is minimal public information on Therm and the GHG calculations are based off of similar products on the market.
Swegon | PACIFIC | Website | Energy Distribution | Heating, Cooling, Ventilation | Hydronic Systems | - | Climate Beam | All | Integrated climate beam with cooling, heating and ventilation - allows for extract airfloor as well. | 6 - 10% | 6 - 10% | 0.97% | 1.42% | Efficiency | Reduces distribution energy when compared to fan based systems. | Medium-term Payback | Chilled beams allow decoupling of sensible loads from ventilation air and allow for reduced duct sizes and higher ceiling heights. | Global Best Practice | N/A | Low | Requires careful monitoring of dew points and surface temperatures to prevent condensation. | Markham, Ontario, Canada | N/A | Established | 200+ Employees | (416) 291-7371 info-na@swegon.com | [9 empty] | Energy efficiency and established credibility |  |  | Renovation of Tenant Space |  | Not favorable for Covid. Recirculates air without filtration.
Swegon | ADRIATIC VF | Website | Energy Distribution | Heating, Cooling, Ventilation | Hydronic Systems | - | Active Climate Beam | All | Active climate beam with cooling, heating and ventilation - allows for adjustable airflow discharge direction and airflow rate. | 11 - 20% | 11 - 20% | 1.84% | 2.61% | Efficiency | Reduces distribution energy when compared to fan based systems. | Medium-term Payback | Chilled beams allow decoupling of sensible loads from ventilation air and allow for reduced duct sizes and higher ceiling heights. | Global Best Practice | N/A | Low | Requires careful monitoring of dew points and surface temperatures to prevent condensation. | Markham, Ontario, Canada | N/A | Established | 200+ Employees | (416) 291-7371 info-na@swegon.com | [9 empty] | Energy efficiency and established credibility |  |  | Renovation of Tenant Space |  | Not favorable for Covid. Recirculates air without filtration.
Swegon | FRB | Website | Energy Distribution | Cooling | Hydronic Systems | - | Passive Chilled Beam | All | Exposed passive chilled beam for suspended installation | 6 - 10% | 6 - 10% | 0.97% | 1.42% | Efficiency | Reduces distribution energy when compared to fan based systems. | Medium-term Payback | Chilled beams allow decoupling of sensible loads from ventilation air and allow for reduced duct sizes and higher ceiling heights. | Global Best Practice | N/A | Low | Requires careful monitoring of dew points and surface temperatures to prevent condensation. | Markham, Ontario, Canada | N/A | Established | 200+ Employees | (416) 291-7371 info-na@swegon.com | [9 empty] | Energy efficiency and established credibility |  |  | Renovation of Tenant Space |  | Not favorable for Covid. Recirculates air without filtration.
Sigma | Valance | Website | Energy Distribution | Heating, Cooling | Hydronic Systems | - | Valance System | All | Induction units that provide cooling/heating with a 2 or 4 pipe circulating chilled/heated water through coils. Innovative optional drainage system. | 6 - 10% | 11 - 20% | 1.45% | 2.27% | Efficiency | Reduces distribution energy when compared to fan based systems. | Short-term Payback | Potential to be more cost effective than traditional radiant panels due to multi-function and ease of installation | Global Best Practice | N/A | Low | Requires careful monitoring of dew points and surface temperatures to prevent condensation. | Mississigua, ON, Canada | N/A | Established | 51-200 Employees | 905-670-3200 sigma@sigmaproducts.com | [9 empty] | Energy efficiency and established credibility |  |  | Renovation of Tenant Space |  | Not favorable for Covid. Recirculates air without filtration.
Fisonic Energy Solutions | FisonicMax | Website | Energy Distribution | Heating, Cooling | Steam Radiators | - | Steam-to-HW Heat Exchanger | All | High-efficiency two-phase flow heat exchanger for domestic hot water service. Water circulated for space heating is heated by direct contact with steam, reducing or eliminating the need for conventional heat exchangers with electric pumps. | 11 - 20% | 21 - 30% | 2.54% | 3.44% | Efficiency | Pulls energy out of steam condensate that would otherwise be wasted. Reduces water used for tempering steam condensate as required in NYC code. | Short-term Payback | High potential steam reduction expected to offset capital cost (heat exchanger should be relatively inexpensive to manufacture) | Emerging | 9 | Low | New technology. | New York, NY, USA | N/A | Growth | 51-200 Employees | 212-732-3777 | [9 empty] | Energy efficiency and established credibility |  |  | Chiller/Boiler Replacement | http://fisonicsolutions.com/ https://www1.nyc.gov/assets/dcas/downloads/pdf/energy/energyinnovation/Phase3_2.pdf
Endo Enterprises | Endotherm and EndoCool | Website | Energy Distribution | Heating, Cooling | Hydronic Systems | - | Heat Transfer Fluids | All | Surfactant type additive for hydronic loops (heating and cooling) that improves heat transfer by reducing surface tension. | 6 - 10% | 6 - 10% | 0.46% | 0.59% | Efficiency | Increased heat transfer in hydronic loops (due to lower surface tension) leads to lower delta T, shorter chiller or boiler run time | Short-term Payback | Low cost, not disruptive. | US Best Practice | N/A | Low | No known / expected O&M risks however product has only been in use for 10 years | Warrington, Cheshire, UK | N/A | Established | 11-50 Employees | dale.edginton@endoenterprises.com 778-895-1990 | 710000000 | 650000 | 25% | 40000000 | 50000 | 50% | 14000000000 | 30000000 | 25% | New technology and approach, establishing credibility |  |  | No Trigger Required |  | Significant third party testing and piloting has been carried out. Product has been adopted for rebate programs by several utilities including one in North America. Won CIBSE award.
Hydromx | Hydromx | Website | Energy Distribution | Heating, Cooling | Hydronic Systems | - | Heat Transfer Fluids | All | Heat transfer fluid with proprietary nano-particle suspension that increases rate of heat transfer | 6 - 10% | 6 - 10% | 0.46% | 0.59% | Efficiency | Increased heat transfer in hydronic loops (due to lower surface tension) leads to lower delta T, shorter chiller or boiler run time | Short-term Payback | Low cost, not disruptive. | US Best Practice | N/A | Low | No know / expected O&M risks however product has only been in use for 10 years | Maspeth, NY, USA | N/A | Growth | 51-200 Employees | INFO@HYDROMX.COM +1(844) 449 3766 | 710000000 | 650000 | 75% | 40000000 | 50000 | 50% | 14000000000 | 30000000 | 75% | New technology and approach, establishing credibility |  |  | No Trigger Required |  | Case studies include Empire State Building. Produdct has been adopted for rebate programs (Xcel) and has won awards.
University of British Columbia, Princeton University, Berkeley and Singapore-ETH | Cold Tube | Website | Energy Distribution | Cooling | Hydronic Systems | - | Radiant cooling panel | All | Condensation free radiative cooling panel using IR transparent film | 6 - 10% | 1 - 5% | 0.15% | 0.12% | Efficiency | Reduces distribution energy and enables low temp heating / higher temperature cooling | Medium-term Payback | Potential to be more cost effective than traditional radiant panels due to multi-function and ease of installation | Emerging | 6 | Medium | Technology under development, polymer film used is not yet robust enough for typical use | Princeton University, Princeton, NJ, USA | Princeton University, Princeton, NJ, USA | Pre-startup | 1-10 Employees | fmeggers@princeton.edu |  | $0/yr | 0% |  | $0/yr | 0% |  | $0/yr | 0% | Emerging technology |  |  | Renovation of Tenant Space | https://news.ubc.ca/2020/08/18/researchers-design-a-new-way-to-stay-cool-in-the-summer/?utm_campaign=&utm_content=1597773639&utm_medium=sprout
Aeroseal | Aeroseal | Website | Energy Distribution | Heating, Cooling, Ventilation | Ducting | - | Duct Sealant | All | Aerosol applied ductwork Sealant | 1 - 5% | 1 - 5% | 0.11% | 0.1% | Efficiency | Reduces leakage in ductwork | Medium-term Payback | 7-10 year payback for typical commercial supply/return, 1-3 year payback for exhaust systems as per Aeroseal white paper. | US Best Practice | N/A | Low | No Substantial Risk. | Miamisburg, OH, USA | N/A | Established | 51-200 Employees | info@aeroseal.com | [9 empty] | Can be expensive, savings vary considerably based on air distribution |  |  | No Trigger Required
Aeroseal | Aerobarrier | Website | Energy Distribution | Heating, Cooling, Ventilation | Ceiling Plenum and Envelopes | Return air plenums | Envelope air sealant | Commercial | Aerobarrier is a aerosol applied envelope sealing product. Application to ceiling plenums to reduce distribution losses has been proposed. | 6 - 10% | 6 - 10% | 0.17% | 0.18% | Efficiency | Reduces leakage in plenums | Medium-term Payback | Payback is speculative as this would be a new application of the technology, expected to be in the range of aeroseal | Emerging | 4 | High | New application has not been tested | Miamisburg, OH, USA | N/A | Established | 51-200 Employees | info@aeroseal.com |  | $0/yr | 0% |  | $0/yr | 0% |  | $0/yr | 0% | New concept, has not been tested. Limited to building's with plenums |  |  | Renovation of Tenant Space |  | Suggested by Prof. Mark Modera (UC Davis) Inventor of aerobarrier
Interpanel GmbH | Interpanel Climatelight and Climatepanel | Website | Energy Distribution | Heating, Cooling | Hydronic Systems | - | Radiant Ceiling Panel | Commercial | Suspended integrated ceiling panel, providing condensation free radiant cooling (through IR transmissive polymer film), radiant heating and lighting. | 6 - 10% | 11 - 20% | 1.6% | 1.94% | Efficiency | Reduces distribution energy and enables low temp heating / higher temperature cooling | Medium-term Payback | Potential to be more cost effective than traditional radiant panels due to multi-function and ease of installation | Global Best Practice | N/A | Medium | New technology, possible durability concerns if panel does not remain sealed to airflow | Crossen, Germany | N/A | Startup/Launch | 11-50 Employees | info@interpanel.com Tel.: +49 (0)36693 434 220 | [9 empty] | New technology, not widely known |  |  | Renovation of Tenant Space
EcoDrain | A1000 Greywater heat exchanger | Website | Energy Distribution | Website | DHW Heat Recovery | - | Drainline Heat Exchanger, Drain Water Heat Recovery | Residential | Horizontal drain heat recovery device, which can reduce hot water use at point of use such as shower and fit in limited space. | 1 - 5% | 1 - 5% | 0.23% | 0.28% | Efficiency | Preheats domestic hot water, reducing load on hot water heating equipment as well as equipment size. | Medium-term Payback | Current products are established to have medium term paybacks, potential cost reduction as products scale to larger manufacturing volumes. | Emerging | 8 | Medium | Though design and testing suggests clogging will not be an issue, long term or real world performance has not been tested | Montreal, Canada | N/A | Growth | 1-10 Employees | sales@ecodrain.com |  | $0/yr | 0% |  | $0/yr | 0% |  | $0/yr | 0% | Currently not in production, has not yet achieved certification for compliance with codes. |  |  | Renovation of Tenant Space |  | Recognized by title 24, IATMO now has certification pathway but EcoDrain has not yet gone through certification (as looking for market)
Renewability Energy | Power-Pipe | Website | Energy Distribution | DHW | DHW Heat Recovery | Access to 6' of drain pipe | drainline heat exchanger, drain water heat recovery | Residential | Vertical drain heat recovery device that replaces section of drain line (typically 6') and works as a counterflow heat exchanger to preheat incoming water flowing into domestic hot water system. | 1 - 5% | 1 - 5% | 0.23% | 0.28% | Efficiency | Preheats domestic hot water, reducing load on hot water heating equipment as well as equipment size. | Medium-term Payback | Current products are established to have medium term paybacks, potential cost reduction as products scale to larger manufacturing volumes. | US Best Practice | N/A | Low | None | Kitchener, Ontario, Canada | Hazleton, PA | Established | 11-50 Employees | info@RenewABILITY.com 1-(877) 606-5559 | [9 empty] | Expensive, also requires specific plumbing / space configuration with access to vertical pipe and proximity to water heating system |  |  | No Trigger Required
EcoDrain | VT1000 | Website | Energy Distribution | DHW | DHW Heat Recovery | Access to 6' of drain pipe | drainline heat exchanger, drain water heat recovery | Residential | Vertical drain heat recovery device that replaces section of drain line (typically 6') and works as a counterflow heat exchanger to preheat incoming water flowing into domestic hot water system. | 1 - 5% | 1 - 5% | 0.23% | 0.28% | Efficiency | Preheats domestic hot water, reducing load on hot water heating equipment as well as equipment size. | Medium-term Payback | Current products are established to have medium term paybacks, potential cost reduction as products scale to larger manufacturing volumes. | Global Best Practice | N/A | Low | None | Montreal, Canada | N/A | Growth | 1-10 Employees | sales@ecodrain.com | [9 empty] | Expensive, also requires specific plumbing / space configuration with access to vertical pipe and proximity to water heating system |  |  | No Trigger Required
EcoDrain | B1000 | Website | Energy Distribution | DHW | DHW Heat Recovery | Access to 6' of drain pipe | drainline heat exchanger, drain water heat recovery | Residential | Horizontal heat recovery device for sewer line (blackwater). | 1 - 5% | 1 - 5% | 0.23% | 0.28% | Efficiency | Preheats domestic hot water, reducing load on hot water heating equipment as well as equipment size. | Medium-term Payback | Current products are established to have medium term paybacks, potential cost reduction as products scale to larger manufacturing volumes. | Global Best Practice | N/A | Low | None | Montreal, Canada | N/A | Growth | 1-10 Employees | sales@ecodrain.com | [9 empty] | Currently not in production, has not yet achieved certification for compliance with codes |  |  | No Trigger Required
[Design Concept] | DC Power Distribution | https://www.emergealliance.org/ | Energy Distribution | Electrical | Distribution | DC compatible equipment | - | All | Direct Current (DC) power distribution avoids conversion losses typical throughout Alternating Current distribution systems, including inverters and rectifiers. For buildings with solar PV inverter losses are avoided, and DC can directly power lighting and other loads (avoiding AC to DC conversion at device level as well). | - | - | - | - | Enabler | DC Power distribution can enable easier implementation of distributed resources (e.g. storage, solar) and more efficient DC powered loads (e.g. lighting) | - | Significant savings on wiring is possible as low voltage DC is touch safe. Less need for inverters and rectifiers in a building with distributed DC resources. | US Best Practice | N/A | - | - | - | - | - | - | - | [9 empty] | AC power has been the dominant in-building distribution strategy for a century. Increased interest in DC power as distributed resources like solar/storage become popular. |  |  | Electrical System Upgrade
[Design Concept] | Phased in floor by floor water loop heat pumps |  | Energy Distribution |  |  |  |  | Commercial | Design concept and approach emerging in NYS is to retrofit in water-water heat pumps for each floor during tenant refresh. Can enable sharing of heat and cooling loads between different zones |  |  |  |  | Efficiency |  |  |  | US Best Practice | N/A
Phase Change Energy Solutions | ENRG Blanket | Website | Thermal Storage | Building Structure, Heating, Cooling | Walls, Ceilings, Partitions | - | Passive PCM Storage | All | BioPCM Phase change material to actively stabilize interior temperature. | 6 - 10% | 6 - 10% | 0.9% | 0.9% | Efficiency & Demand Flexibility | Decreases HVAC runtime and allows for demand flexibility practices. | Long-term Payback | Assumes significant retrofit cost for existing buildings. | US Best Practice | N/A | Medium | Substantial interior retrofit required | Asheboro, NC, USA | N/A | Established | 51-200 Employees | Website Contact Form or 1-800-283-7887 or 1-336-629-3000 | [9 empty] | Not widely established, favorable economics significant time of use varation in utility rates | 1 Million SF | 8 Million SF | Renovation of Tenant Space
Phase Change Energy Solutions | Phasestor | Website | Thermal Storage | Heating, Cooling | Chilled water system, or hydronic heating system | - | Active Cold Storage (PCM) | All | Storage tank that can be used for hot water or cold water storage depending on PCM selection. | < 1% | 11 - 20% | 0.11% | 2.5% | Demand Flexibility | Carbon reduction based on chilled water application enabling load flexibility optimized for carbon reduction | Medium-term Payback | Assumes project specific cost would meet reasonable ROI. | US Best Practice | N/A | Low | No substantial risk | Asheboro, NC, USA | N/A | Established | 51-200 Employees | Website Contact Form or 1-800-283-7887 or 1-336-629-3000 | [9 empty] | Not widely established, favorable economics significant time of use varation in utility rates |  |  | Chiller/Boiler Replacement
Phase Change Energy Solutions | ENRG Panel | Website | Thermal Storage | Building Structure, Heating, Cooling | Walls, Ceilings, Partitions | - | Passive PCM Storage | All | Rigid panel system that integrates sheets of ENRG Blanket into a 2'x2' shell (See ENRG Blanket). | 6 - 10% | 6 - 10% | 0.9% | 0.9% | Efficiency & Demand Flexibility | Decreases HVAC runtime and allows for demand flexibility practices. | Medium-term Payback | Assumes project specific cost would meet reasonable ROI. | US Best Practice | N/A | Medium | Substantial interior retrofit required | Asheboro, NC, USA | N/A | Established | 51-200 Employees | Website Contact Form or 1-800-283-7887 or 1-336-629-3000 | [9 empty] | Not widely established, favorable economics significant time of use varation in utility rates |  |  | Renovation of Tenant Space
Calmac | IceBank | Website | Thermal Storage | Cooling | Chilled Water System | - | Ice Storage | Commercial | Ice storage tank with a welded counter-flow and polyethylene heat exchanger. | < 1% | 11 - 20% | 0.11% | 2.5% | Demand Flexibility | Carbon reduction is dependent on aligning with grid resources. | Medium-term Payback | Assumes project specific cost would meet reasonable ROI. | US Best Practice | N/A | Low | No substantial risk | Fair Lawn, NJ, USA | N/A | Established | 200+ Employees | Website Contact Form or 201-797-1511 | [9 empty] | Highly dependant on utility rates and demand charges. Large footprint. |  |  | Chiller/Boiler Replacement
FAFCO | IceStor | Website | Thermal Storage | Cooling | Chilled Water System | - | Ice Storage | Commercial | Ice Storage | < 1% | 11 - 20% | 0.11% | 2.5% | Demand Flexibility | Carbon reduction is dependent on aligning with grid resources. | Medium-term Payback | Assumes project specific cost would meet reasonable ROI. | US Best Practice | N/A | Low | No substantial risk | Chico, CA, USA | N/A | Established | 11-50 Employees | Website Contact Form or (800) 994-7652 (530) 332-2100 | [9 empty] | Highly dependant on utility rates and demand charges. Large footprint. |  |  | Chiller/Boiler Replacement
Active Energy Systems | Ice Chiller | Website | Thermal Storage | Cooling | Chilled Water System | - | Ice Storage | Commercial | Icephobic heat exchanger integrated into an "ice chiller" which takes in liquid water and returns an ice slurry. | < 1% | 11 - 20% | 0.11% | 2.5% | Demand Flexibility | Carbon reduction is dependent on aligning with grid resources. | Medium-term Payback | Assumes project specific cost would meet reasonable ROI. | US Best Practice | N/A | Low | No substantial risk | Knoxville, TN, USA | N/A | Growth | 1-10 Employees | Website Contact Form | [9 empty] | Highly dependant on utility rates and demand charges. Large footprint. |  |  | Chiller/Boiler Replacement |  | proprietary heat exchanger which doesnt create ice layer on coil
Baltimore Aircoil | Ice Thermal Storage | Website | Thermal Storage | Cooling | Chilled Water System | - | Ice Storage | Commercial | Ice Storage Container and Coil system | < 1% | 11 - 20% | 0.11% | 2.5% | Demand Flexibility | Carbon reduction is dependent on aligning with grid resources. | Medium-term Payback | Assumes project specific cost would meet reasonable ROI. | US Best Practice | N/A | Low | No substantial risk | Jessup, Maryland, USA | N/A | Established | 200+ Employees | Website Contact Form | [9 empty] | Highly dependant on utility rates and demand charges. Large footprint. |  |  | Chiller/Boiler Replacement
InsolCorp | Infinite R™ | Website | Thermal Storage | Heating, Cooling | Building Envelope, Interior Partitions | - | Passive PCM Storage | All | Phase change material to actively stabilize interior temperature | 6 - 10% | 6 - 10% | 0.9% | 0.9% | Efficiency & Demand Flexibility | Decreases HVAC runtime and allows for demand flexibility practices. | Medium-term Payback | With no rebate, case studies show 2-4 years | US Best Practice | N/A | Medium | Significant retrofit | Albemarle, NC, USA | N/A | Growth | 11-50 Employees | Pete Horwath, CEO pete@insolcorp.com | $40 billion |  |  | $2.4 billion |  |  |  | $820 billion |  | Not widely established, favorable economics significant time of use varation in utility rates |  |  | Renovation of Tenant Space
Enkoat |  | Website | Thermal Storage | Heating, Cooling | Building Envelope, Interior Partitions | - | Passive PCM Storage | All | Adaptive insular coating - embeds a PCM into paint/plaster/stucco for interior and exterior applicability. | 6 - 10% | 6 - 10% | 0.9% | 0.9% | Efficiency | Decreases HVAC runtime and allows for demand flexibility practices. | Medium-term Payback | Assumes project specific cost would meet reasonable ROI | Emerging | 5 | Low | Technology is not on the market | Casa Grande, AZ, USA | N/A | Pre-startup | 1-10 Employees | Website Contact Form |  | $0/yr | 0% |  | $0/yr | 0% |  | $0/yr | 0% | Technology not yet available |  |  | Renovation of Tenant Space | 1. https://youtu.be/_iKxzKb3X_c
Techstyle Materials |  | Video Pitch | Thermal Storage | Heating, Cooling | Building Envelope, Interior Partitions | Drywall replacement | Passive PCM Storage | All | 1mm thick material for sheathing/drywall with PCM, allowing for heat/vapor control and relative humidity buffering | 1 - 5% | 1 - 5% | 0.45% | 0.45% | Efficiency & Demand Flexibility | Decreases HVAC runtime and allows for demand flexibility practices. | Medium-term Payback | thickness is minimal in comparison to other envelope PCM, so payback is longer | Emerging | 2 | Low | Technology seems to be in the concept stage | Somerville, Massachusetts, USA | N/A | Pre-startup | 1-10 Employees | info@techstylematerials.com |  | $0/yr | 0% |  | $0/yr | 0% |  | $0/yr | 0% | Technology not yet available |  |  | Renovation of Tenant Space | http://www.techstylematerials.com/ | Product is only at concept stage. Integration of phase change into drywall is a promising idea. Only validated at concept level as limited info is available at this time.
Cryogel | Ice Balls | Website | Thermal Storage | Cooling | Chilled Water System | - | Ice Storage | All | Ice Storage using small expandable "ice balls". | < 1% | 11 - 20% | 0.11% | 2.5% | Demand Flexibility | Carbon reduction is dependent on aligning with grid resources. | Medium-term Payback | Assumes project specific cost would meet reasonable ROI | Global Best Practice | N/A | Low | Technology is not on the market | San Diego, CA, USA | N/A | Established | 11-50 Employees | Tel: 858.457.1837 email: tes@cryogel.com | [9 empty] | Highly dependant on utility rates and demand charges. Large footprint. |  |  | Chiller/Boiler Replacement
Global-E-Systems | Thermavar | Website | Thermal Storage | Cooling | Ceiling, Air Diffusers, Terminal Units | - | Passive PCM Storage | All | Ceiling diffuser panel with PCM for thermal storage & passive cooling capacity | 6 - 10% | 6 - 10% | 0.9% | 0.9% | Efficiency & Demand Flexibility | Decreases HVAC runtime and allows for demand flexibility practices. | Medium-term Payback | Assumes project specific cost would meet reasonable ROI | Global Best Practice | N/A | Medium | Requires substantial interior retrofit | Dordrecht, Netherlands | N/A | Growth | 1-10 Employees | Website Contact Form or +31 (0)78 6931 225 |  | $0/yr | 0% |  | $0/yr | 0% |  |  |  | Tennant disruption, cost |  |  | Renovation of Tenant Space |  | Used in the Kuala Lumpur City Center
Department of Energy (DoE), Lawrence Berkeley National Lab (LBNL), National Renewable Energy Laboratory (NREL) | N/A | Website | Thermal Storage | Building Structure, Heating, Cooling | Walls, Ceilings, Partitions | - | Passive PCM Storage | all | Solid state tunable PCM (material can be applied to surfaces of a building) for thermal energy storage and switches for smart building envelopes | 6 - 10% | 6 - 10% | 0.9% | 0.9% | Efficiency & Demand Flexibility | Decreases HVAC runtime and allows for demand flexibility practices. | Medium-term Payback | Assumes project specific cost would meet reasonable ROI | Emerging | 2 | Medium | Technology is not on the market | US DOE | N/A | Pre-startup | 1-10 Employees | Roderick.Jackson@nrel.gov rsprasher@lbl.gov cdames@berkeley.edu |  | $0/yr | 0% |  | $0/yr | 0% |  | $0/yr | 0% | Not yet established |  |  | Full Major Building Retrofit
McDermott | Strata-Therm | Website | Thermal Storage | Cooling | Chilled Water System | - | Active Cold Storage | All | CB&I Strata-Therm thermal energy storage (TES) tanks and SoCool fluid that stratifies water to take advantage of low temps at the bottom of the tank | < 1% | 11 - 20% | 0.11% | 2.5% | Demand Flexibility | Carbon reduction is dependent on aligning with grid resources. | Medium-term Payback | Assumes project specific cost would meet reasonable ROI | US Best Practice | N/A | High | No building specific application | Houston, TX, USA | N/A | Established | 200+ Employees | Website Contact Form | [9 empty] | Highly dependant on utility rates and demand charges. Large footprint. |  |  | Chiller/Boiler Replacement
Rubitherm GmbH | CSM Macro-encapsulation | Website | Thermal Storage | Building Structure, Heating, Cooling | Ceiling | - | Passive PCM Storage |  | Small Aluminum incased PCM panels for application in drop ceilings or other. PCM options that have heat storage capacity ranging from 170-210 kJ/kg | 6 - 10% | 6 - 10% | 0.9% | 0.9% | Efficiency & Demand Flexibility | Decreases HVAC runtime and allows for demand flexibility practices. | Medium-term Payback | Assumes project specific cost would meet reasonable ROI | Global Best Practice | N/A | Medium | Required substantial interior retrofit | Berlin, Germany | N/A | Startup/Launch | 1-10 Employees | info@rubitherm.com |  | $0/yr | 0% |  | $0/yr | 0% |  |  |  | Not widely established, favorable economics significant time of use varation in utility rates |  |  | Renovation of Tenant Space
ETH Zurich | PCM ceiling panel | Link | Thermal Storage | Building Structure, Heating, Cooling | Ceiling | - | Passive PCM Storage | All | A PCM ceiling panel design that is optimized for retrofits, ideal for use in lightweight structures. | 6 - 10% | 6 - 10% | 0.9% | 0.9% | Efficiency & Demand Flexibility | Decreases HVAC runtime and allows for demand flexibility practices. | Medium-term Payback | Assumes project specific cost would meet reasonable ROI | Emerging | 8 | Medium | Requires substantial interior retrofit; not available yet | ETH Zurich | N/A | Pre-startup | 1-10 Employees | markus.koschenz@hslu.ch |  | $0/yr | 0% |  | $0/yr | 0% |  | $0/yr | 0% | pre-start up |  |  | Renovation of Tenant Space
CREATE project | Heating Storage | Link | Thermal Storage | Heating | Hydronic Heating System | - | Thermochemical Heat Storage | All | Long duration thermal chemical heat storage in salt hydrate (k2CO3) | < 1% | < 1 % | 0.1% | 1.5% | Efficiency & Demand Flexibility | Carbon reduction is dependent on aligning with grid resources. | Long-term Payback | Cost optimization might not align with carbon optimization | Emerging | 7 | Medium | Applied in single family residential, needs to be scaled for distributed storage in larger buildings | Eindhoven, Netherlands | N/A | Pre-startup | 1-10 Employees | Eindhoven Institute of Tech |  | $0/yr | 0% |  | $0/yr | 0% |  | $0/yr | 0% | pre-start up |  |  | Full Major Building Retrofit
Evapco | ICE-PAK® | Website | Thermal Storage | Cooling | Chilled Water System | - | Ice Storage | Commercial | Containerized insulated ice storage units. | < 1% | 11 - 20% | 0.11% | 2.5% | Demand Flexibility | Cuts down electrical loads during peak periods. Can reduce size of central cooling plant. | Short-term Payback | Utility rate structure and downsizing of primary cooling plant. | Global Best Practice | N/A | High | Requires a dedicated Glycol Chiller system for Ice generation. | Westminster, MD, USA | N/A | Established | 200+ Employees | richard.mullen@evapco.com | [9 empty] | Highly dependant on utility rates and demand charges. Large footprint. |  |  | Full Major Building Retrofit
Evapco | Extra-PAK® | Website | Thermal Storage | Cooling | Chilled Water System | - | Ice Storage | Commercial | Energy storage with proprietary coil technology to increased conversion efficiency. Requires concrete basin or site fabricated tank. Approx. half the cost of ICE-PAK by comparison. | < 1% | 11 - 20% | 0.11% | 2.5% | Demand Flexibility | Cuts down electrical loads during peak periods. Can reduce size of central cooling plant. | Short-term Payback | Utility rate structure and downsizing of primary cooling plant. | Global Best Practice | N/A | High | Requires a dedicated Glycol Chiller system for Ice generation. | Westminster, MD, USA | N/A | Established | 200+ Employees | richard.mullen@evapco.com | [9 empty] | Highly dependant on utility rates and demand charges. Large footprint. |  |  | Full Major Building Retrofit
Dunham-Bush Americas | ICE-CEL | Website | Thermal Storage | Cooling | Chilled Water System | - | Ice Storage | All | Ice storage systems available as an integrated system with air-cooled chillers or as a tube-in-tank thermal storage system | < 1% | 11 - 20% | 0.11% | 2.5% | Demand Flexibility | Cuts down electrical loads during peak periods. Can reduce size of central cooling plant. | Short-term Payback | Utility rate structure and downsizing of primary cooling plant. | Global Best Practice | N/A | Low | Limited to small applications. 80-ton chiller max on packaged, skid-mounted units. Larger sizes available for engineered systems. | Miramar, FL, USA | N/A | Established | 200+ Employees | info@dbamericas.com; Justin Hogan Justin@dbamericas.com | [9 empty] | Dependant on periods cheap electricity for ice generation. |  |  | Chiller/Boiler Replacement
SHARC Energy Systems | Sharc Thermal Energy Recovery System | Website | Thermal Storage | Heating, Cooling, DHW | Hydronic Heating, Chilled Water Systems | Requires connection to sewer system | Wastewater Heat Recovery | All | Wastewater thermal energy recovery system. Commercial-sized system that pumps wastewater through filtration system that separates solids and sends the remaining liquid waste water to a heat pump system. Requires a holding tank as part of the system. | 31-40% | 41-50% | 6.06% | 7.25% | Efficiency | Heat Recovery from waste water. | Medium-term Payback | Adds an additional, sustainable source of energy for heating and cooling. | Global Best Practice | N/A | High | Requires a connection and basin for wastewater and space for pumping equipment. Some owners may not want to maintain wastewater systems. | Port Coquitlam, BC, Canada | N/A | Growth | 11-50 Employees | 604-475-7710 ext. 2001 | [9 empty] | Requires a connection and basin for wastewater and space for pumping equipment. Some owners may not want to maintain wastewater systems. |  |  | Full Major Building Retrofit | https://highmark.co/insights/sharc-intro-flyer/ https://highmark.co/technologies/sharc-wastewater-energy-recovery/
SHARC Energy Systems | Piranha Thermal Energy Recovery System | Website | Thermal Storage | Heating, Cooling, DHW | Hydronic Heating, Chilled Water Systems | Requires connection to sewer system | Wastewater Heat Recovery | All | Wastewater thermal energy recovery system. Packaged heat pump using waste water for energy source. Pumps, filters and returns the waste water. Requires a holding tank. Used in smaller buildings primarily residential. | 31-40% | 41-50% | 6.06% | 7.25% | Efficiency | Heat Recovery from waste water. | Medium-term Payback | Adds an additional, sustainable source of energy for heating and cooling. | Global Best Practice | N/A | High | Requires a connection and basin for wastewater and space for pumping equipment. Some owners may not want to maintain wastewater systems. | Port Coquitlam, BC, Canada | N/A | Growth | 11-50 Employees | 604-475-7710 ext. 2001 | [9 empty] | Requires a connection and basin for wastewater and space for pumping equipment. Some owners may not want to maintain wastewater systems. |  |  | Full Major Building Retrofit | https://highmark.co/insights/sharc-intro-flyer/ https://highmark.co/technologies/sharc-wastewater-energy-recovery/
Rabtherm | Rabtherm | Website | Thermal Storage | Heating, Cooling | Hydronic Heating, Chilled Water Systems | Requires new sewer mains. | Wastewater Heat Recovery | All | Sewer heat recovery system with heat exchangers embedded directly into sewer pipes. Can be used with any type of heat pump. | 11 - 20% | 11 - 20% | 2.36% | 2.84% | Efficiency | Heat Recovery from waste water in underground sewer pipes. | Medium-term Payback | Adds an additional, sustainable source of energy for heating and cooling. | Global Best Practice | N/A | High | Requires civil/site work to implement. Requires high sewer load at the site. | Germany | N/A | Established | 200+ Employees | usa@rabtherm.com | [9 empty] | Difficult to retrofit. |  |  | Full Major Building Retrofit | http://www.rabtherm.com/en/produkte.html
Syracuse University | Micro Environmental Control System (μX) | ARPA-E | Thermal Storage | Heating, Cooling | Zone/Terminal Equipment | This system still requires a ventilation system with dehumidification. | Occupant-Level Cooling | All | Micro-scroll (vapor) compressor coupled to a phase-change material for thermal storage to provide desk level individual cooling (reducing peak demand) and heating. | 1 - 5% | 1 - 5% | 0.59% | 0.7% | Efficiency & Demand Flexibility | Conditioning occupants locally enables the relaxing of temperature setpoints outside of typical comfort range - decreasing HVAC energy. Demand flexibility practices can cuts down on electrical load during peak periods. | Medium-term Payback | Lowering of PCM cost, utility rate structure and downsizing of primary cooling plant. | Emerging | 7 | Low | Reliance on individuals to control temperature as opposed to centralized temperature is relatively uncharted. | Syracuse, New York, USA | N/A | Pre-startup | 1-10 Employees | Dr. H Ezzat Khalifa hekhalif@syr.edu |  | $0/yr | 0% |  | $0/yr | 0% |  | $0/yr | 0% | Pre-start up |  |  | No Trigger Required |  | * Calcium chloride hexahydrate (29C). 80 to 90 kWh/m3 storage capacity at 22-36C. 10-15 kW power at 7 C delta T. -Great for retrofits, since it doesn't involve huge tenant disruption *They have also spoken with a potential manufacturer in New York. * Won the ARPA-E Award: DE-AR0000526 * https://www.youtube.com/watch?v=XkT03J0xADw&ab_channel=SyracuseCoE
Cristopia Energy Systems | STL | Product Info | Thermal Storage | Cooling | Chilled Water System | - | Phase Change Cold Storage | Commercial | Encapsulated phase change materials in storage tanks (1 mm sphere with polyolefins) | < 1% | 11 - 20% | 0.11% | 2.5% | Demand Flexibility | Carbon reduction is dependent on aligning with grid resources. | Medium-term Payback | Assumes project specific cost would meet reasonable ROI | Global Best Practice | N/A | Low | most applications are in Europe | Vence, France | Highmark Building Efficient, NYC, NY | Startup/Launch | 1-10 Employees | HIGHMARK richard@highmark-ny.com | [9 empty] | Highly dependant on utility rates and demand charges. Large footprint. |  |  | Chiller/Boiler Replacement
ZAE Bayern | VSI Storage Tank |  | Thermal Storage | DHW, Heating | Hydronic Heating System | - | Hot Water Storage Tank | All | Vacuum insulated hot water storage tank (perlite in cavity) for long duration storage | 1 - 5% | 1 - 5% | 0.09% | 0.11% | Efficiency & Demand Flexibility | Reduces losses for DHW storage, can be used for heat storage | Medium-term Payback | Expected to be medium to long term payback based on technology type and complexity | Emerging | 8 | Medium | Vacuum seal may be hard to maintain over time | Garching, Germany | ZAE Bayern - Energy Storage Walther-Meißner-Str. 6 85748 Garching | Pre-startup | 11-50 Employees | Christoph Rathgeber, Deputy Head of Group Thermal Energy Storage, Tel.: +49 89 329442-88, christoph.rathgeber@zae-bayern.de |  | $0/yr | 0% |  | $0/yr | 0% |  | $0/yr | 0% | Pre-start up |  |  | Chiller/Boiler Replacement
ZAE Bayern and Clina | Latent heat storage with capillary tube heat exchanger | Website | Thermal Storage | DHW, Heating | Hydronic Heating System | - | Active Phase Change Heat Storage | All | Salt hydrate phase change storage using capillary tube heat exchanger, achieving 80-90 kWh(th)/m3 storage density | < 1% | < 1 % | 0.11% | 1.5% | Demand Flexibility | Enables heating energy use to be shifted to periods when grid carbon is lowest (assuming changing with a heat pump or other electric source) | Medium-term Payback | Uncertain cost, likely to reflect other phase change systems | Emerging | 8 | Medium | Some risk of loosing vacuum seal if damage | Garching, Germany | ZAE Bayern - Energy Storage Walther-Meißner-Str. 6 85748 Garching | Pre-startup | 11-50 Employees | Christoph Rathgeber, Deputy Head of Group Thermal Energy Storage, Tel.: +49 89 329442-88, christoph.rathgeber@zae-bayern.de |  | $0/yr | 0% |  | $0/yr | 0% |  | $0/yr | 0% | Pre-start up |  |  | Chiller/Boiler Replacement
ZAE Bayern | Phase change salt hydrate slurry |  | Thermal Storage | Cooling | Chilled Water System | - | Active Phase Change Cooling | All | Salt hydrate slurry (K2HPO4·6H2O) targeting 15C enabling 5x increased storage capacity compared with water. Could be pumpable for higher density energy delivery. | 6 - 10% | 6 - 10% | 0.2% | 0.1% | Efficiency & Demand Flexibility | Could minimize distribution energy due to high energy density, could enable thermal storage within cooling loop (savings based on efficiency only) | Medium-term Payback | Uncertain cost, though may reflect that of other phase change materials plus additional specialized pumps | Emerging | 6 | High | Many unknowns around pumping salt hydrates | Garching, Germany | ZAE Bayern - Energy Storage Walther-Meißner-Str. 6 85748 Garching | Pre-startup | 11-50 Employees | Christoph Rathgeber, Deputy Head of Group Thermal Energy Storage, Tel.: +49 89 329442-88, christoph.rathgeber@zae-bayern.de |  | $0/yr | 0% |  | $0/yr | 0% |  | $0/yr | 0% | Pre-start up |  |  | Chiller/Boiler Replacement |  | Significantly higher energy storage density than hot water storage
Sunamp | UniQ heat batteries | Website | Thermal Storage | DHW, Heating | Hydronic Heating System | - | Active Phase Change Heat Storage | All | Modular phase change storage 'battery' for residential DHW or space heating, which can be charged with electric or hydronic heat. Replaces a conventional water heater tank and acts as a low loss 'on demand' hot water heater with PCM temp of 136F. | 1 - 5% | 1 - 5% | 0.09% | 0.11% | Efficiency & Demand Flexibility | Compact storage relative to domestic hot water heater could enable greater thermal storage enabling better load flexibility, as well as lower losses due to storage temperature and surface area | Long-term Payback | Pricing unavailable for US market, however PCM is typically fairly expensive | Global Best Practice | N/A | Medium | Product is relatively new so limited long term data (though accelerated cycle testing indicates long life) | 1 Satellite Park, Macmerry, East Lothian, EH33 1RY, Scotland | none | Startup/Launch | 11-50 Employees | info@sunamp.com +44 (0)1875 610001 | [9 empty] | New product, PCM has traditionally been expensive |  |  | Chiller/Boiler Replacement
Rubitherm GmbH | Phasecube | Website | Thermal Storage | Heating, Cooling | Chilled water system, or hydronic heating system | - | Active Phase Change Storage | All | Packaged OA unit with PCM for storing cold at night and using it to cool ventilation air during the day. | 1 - 5% | 1 - 5% | 0.11% | 2.5% | Efficiency & Demand Flexibility | Free cooling from phase change material | Long-term Payback | Tall building retrofit would be costly for minor savings | Emerging | 8 | Medium | Major retrofit of central AHU | Berlin, Germany | none | Growth | 11-50 Employees | info@rubitherm.com | [9 empty] | Expensive |  |  | Renovation of Tenant Space
PCM Products | PlusIce PCM S Range Hydrated Salts | Website | Thermal Storage | Heating, Cooling | Chilled water system, or hydronic heating system, envelope, ceiling, floor, | - | Phase Change | All | water-based PCM (specifically the salt hydrate solutions for building application) for a variety of applications,can come prefilled in icepacks or balls, or can be thickened as a paste (building material application), customer can provide container for use | < 1% | 11 - 20% | 0.11% | 2.5% | Demand Flexibility | Enables demand flexibility practices and is an enabler for heat pump storage | Medium-term Payback | Expected to be medium to long term payback based on technology type and complexity | Global Best Practice | N/A | Medium | Case studies are mostly in Europe | Cambridgeshire, UK | N/A | Established | 51-200 Employees | info@pcmproducts.net | [9 empty] | Expensive |  |  | Renovation of Tenant Space |  | most building application now is with hydrated salt options.
[Design Concept] | Topping Slab | Website | Thermal Storage | Floor, Heating, Cooling | Floor | - | Thermal Mass | All | A layer of concrete can be applied via retrofit to provide passive thermal mass to a building. |  |  |  |  | Efficiency | Thermal retention can reduce HVAC equipment size. | - | Lightweight concrete is increasingly affordable. | US Best Practice | N/A | Low | Building weight constraints. | N/A | N/A | N/A | N/A | N/A | [9 empty] | Emerging Idea - Disruption of tenant space |  |  | Renovation of Tenant Space | Relevant Papers: 1. Concrete Floor Soluions for Passive and Active Cooling https://www.concretecentre.com/Publications-Software/Publications/Concrete-Floor-Solutions-for-Passive-and-Active-Co.aspx
[Design Concept] | Storage Source Heat Pump | Link | Thermal Storage | Cooling, Heating | Chilled Water System, Hydronic Heating System | Requires sufficient winter cooling load that is offset from heating loads (eg. office core zone cooling and perimeter morning heating loads) | Storage Source Heat Pump | Commercial | Heat pumps are used to make ice while meeting morning warmup loads, enabling ice to be used later in the day to meet cooling loads. |  |  |  |  | Efficiency | Shifting a building’s thermal consumption across a 24-hour average load allows for smaller/cheaper equipment. | - |  | US Best Practice | N/A | Medium | Proper implementation and controls are necessary for this system to function efficiently. Requires multiple systems to interact. | N/A | N/A | N/A | N/A | N/A | [9 empty] | Emerging Idea - Difficulty of Implementation |  |  | Full Major Building Retrofit
Vortex Bladeless | Vortex Bladeless | website | Power Generation | Electrical |  |  | renewable, on-site generation | All | bladeless wind powered electricity generation: vortex induced vibration resonant wind generator
Thermablock | Thermablock Insulation | website | Building Envelope | Building Structure | Wall, Ceiling, Partition |  | envelope, facade | All | Thermablok aerogel insulating strips may be installed to the stud on the exterior, interior or both sides of the wall framing.
BuildGreen SIPS | MGO Panel | website | Building Envelope | Building Structure | Wall, Ceiling, Partition |  | envelope, facade | All | Fire proof foam facade, MGO (magnesium-oxide) panels
Efforce | WOZX Token | website | Financing | Financing |  |  | financing | All | cryptocurrency for energy savings
Generate Capital |  | website | Financing | Financing |  |  | financing | All
Alturus |  | website | Financing | Financing |  |  | financing | All
Eavor | Eavor-Loop | website | Power Generation | Heating, Electrical | District Heat | deep well drilling required (3500m), 2 stations far apart at the surface (5000m) | renewable | District steam | industrial scale closed loop geothermal, used for commercial heating applications or electricity generation. Closed loop creates thermosyphon effect, eliminating need of ciruclator pumps.
WexEnergy | WindowSkin | website | Building Envelope | Building Structure | Window |  | envelope, facade | All | window insulation panel
Glen Dimplex Heating & Ventilation | Zeroth Energy System | website | Energy Distribution | Heating, Cooling | Thermal distribution system | hydronic plumbing | distribution | All | ambient thermal distribution system providing low temperature water to localized water-sourced heat pump
Ephoca | HPAC 2.0 | website | Heat Pump | Heating, Cooling | HVAC |  | Heat Pump | All | through wall heat pump with minimal facade exposure
SlatX Technology | EnerStore | website | Thermal Storage, Power Storage | Heating, Electrical |  |  | energy storage | All | thermochemical energy storage using nanocoated salt. Can be used as CHP on-site or intermittent renewable energy storage for grid scale. | [12 empty] | Sweden
Hydronic Shell Technologies | Hydronic Shell | website | Building Envelope, Energy Distribution | Heating, Cooling, Ventilation, Building Structure | HVAC, External Wall | Facade requirement | Energy distribution, building envelop | Residential | Facade-Integrated HVAC System. The hydronic shell panel goes over the outer clad of the building, adding insulation, hydronic distribution and air ventilation
EnergyNest | EnergyNest Thermal Battery | website | Thermal Storage | Heating |  |  | Thermal battery | Commercial | Industrial sized thermal battery system, storing heat using thermal mass of steel and concrete called Heatcrete. Provides heating options and can potentially produce electricity |  |  |  |  | Efficiency & Demand Flexibility | store waste heat |  |  | Emerging |  |  |  | Norway
Alpen | Winsert | website | Building Envelope | Building Structure | Window |  | window insert | All | Interior window insert, adding window pane without affecting exterior window. Increases window R value and reduces heat transfer. |  |  |  |  | Efficiency | reduces heat loss/gain through window | [6 empty] | Colorado
Lync | Aegis | website | Heat Pump | Heating, Cooling | Heat Pump | Electrical equirement | Electric heating | All | Natural refrigerant CO2 heat pumps. CO2 or R744 is non-toxic, non-flammable. Air-sourced option produces hot water up to 185F with minimum air temperature of -4F without supplemental heat. Water-sourced option produces hot water up to 185F with minimum water temperature of 14F without supplemental heat. Cool recovery option. |  |  |  |  | Efficiency |  |  |  | US Best Practice |  |  |  |  | Sales representative in Rye Brook and Albany NY
HPS | Picea | website | Power Storage | Heating, Electrical | Battery storage, Heating and DHW | sized for single- or two-family homes | Electricity storage, waste heat | Residential | Picea is a compact battery storage and heating integrated system. Electricity is stored in a 25 kWh battery for short term storage. For long term storage, electricity is used to generate hydrogen via an electrolizer. The hydrogen is stored and used to generate electricity via a fuel cell when needed (300 kWh). Waste heat from the fuel cell and electrolizer is reused to provide heating or hot water. |  |  |  |  | Efficiency & Demand Flexibility |  |  |  | Emerging |  |  |  | Berlin, Germany
Zinc8 | Zinc8 | website | Power Storage | Electrical | Battery storage |  | Electricity storage | All | Zinc-Air Regenerative Fuel Cell System. Stores electricity via zinc and oxygen chemical reaction. Electricity is used to generate zinc particles, releasing oxygen to the atmosphere as a byproduct (charging). Electricity is generated by recombining the zinc particles with oxygen (discharging). |  |  |  |  | Demand Flexibility |  |  |  | Emerging |  |  |  | Canada
Lavo | Lavo | website | Power Storage | Electrical | Hydrogen storage |  | Electricity storage | All | Small hydrogen hybrid battery, 40kWh storage capacity. Generates hydrogen for storage using electricity, can be combined to on-site solar system |  |  |  |  | Demand Flexibility |  |  |  | Emerging |  |  |  | Australia
Energy Machines | Energy Machines | website | Heat Pump | Heating, Cooling, DHW | Heat Pump | Electrical requirement | Electric heating, cooling and hot water | All | Combined chiller and heat pump to provide simultaneous heating and cooling and increase efficiency (up to COP 10). Integrated energy systems based on a heat exchanger between heating and cooling system. |  |  |  |  | Efficiency | [7 empty] | Denmark
Energy Machines | Climate Machines | website | Energy Distribution | Ventilation | ERV | can be customed made for project | AHU with ERV | All | Smart air handling units: energy recovery system with cross-flow flat plate heat exchanger between supply and exhaust air. 90% energy recovery and low operating cost |  |  |  |  | Efficiency | [7 empty] | Denmark
Ectogrid | ectogrid | website | Heat Pump | Heating, Cooling, DHW |  | thermal distribution network |  | All | Combined heat pump and cooling unit to balance energy loads in district setting, enables thermal distribution networks (ambient loop system) and simultaneous heating and cooling between buildings. |  |  |  |  | Efficiency & Demand Flexibility |  |  |  | Emerging |  |  |  | Sweden
Riginabox | RIGINABOXtm | website | Other | Geothermal drilling solution |  |  |  | All | Small drilling rig to make geothermal loops: a portable, powerful and one man operable 100% modular electric driven hydraulic driven system requiring only a 100 AMP Single Phase Panel that enables vertical loop installation both inside and under structures as well as exterior fields | [12 empty] | Chicago
Ihandal | Heatfuse | website | Heat Pump | Heating, Cooling, DHW |  |  |  | All | Turnkey Provider of Sustainable Engineering Solutions
NODA | NODA Building | website | Energy Distribution | Energy Management | Thermal distribution system |  |  | All | AI-based system to optimise heating and cooling in residential and commercial buildings while ensuring a good indoor climate | [12 empty] | Karlshamn, Sweden
Therminer |  | website | Heating Solution | Heating, Cooling, DHW | Boiler plant |  | Boiler | Commercial | Boiler 3.5 kW, hot water output at 85F. IT Equipment thermal waste heat capture. Provides computing power with heat generation
HeatVentors | HeatTank | website | Thermal Storage | Heating, Cooling, DHW |  |  |  | All | Phase Change Materials used for thermal storage. HeatTank serves as an energy buffer with independent control logic.
SOLID Solar Energy Systems |  | website | Heating/Cooling Solution | Heating, Cooling, DHW |  |  | Solar thermal | All | Large scale solar thermal collectors for heating and cooling (absorption heat pumps) applications. Applicable to district steam or replace heating/cooling plant. Proven technology with case studies in Europe, Asia and NA.
Orison | Orison Panel | website | Power Storage | Electrical |  |  |  | All | Wall-mounted battery storage. This 2.2 kWh battery charges and discharges through a typical 110V outlet. This enables distributed curtailment capacity in residential or commercial settings.
Multistack | Range of products | website | Heat Pump | Heating, Cooling | Hydronic Systems |  |  | All | Range of large scale, modular heat pumps - In particular a water to water heat pump that can be combined with geothermal for source/sink
Hitema | Multiple | Website | Heat Pump | Heating, Cooling | heat pump, central cooling/heating |  | heat pump |  | Outside of scope - heat pump. Large capacity reversible heat pumps
TORO WATT | N/A | Website | Heat Pump | Cooling/Heating System |  |  |  | All | Cooling solution. Air cooling seperating sensible & latent cooling w/ electric heat pump
Stash | Energy Heat Pump | Website | Heat Pump | Heating , Cooling | Heat Pump |  | Air-source Heat Pump | All | Cooling/heating solution. Inverter based PTHP with phase change energy storage.
Olimpia Splendid | Maestro | Website | Heat Pump | Heating, Cooling | Heat Pump |  | Air-source Heat Pump | All | Cooling/heating solution. Ductless PTHP with inverter compressor.
Clivet | WLHP | Website | Heat Pump | Heating, Cooling | Hydronic Cooling, Heating |  | Water Loop Heat Pump | All | Cooling/heating solution. Low-temperature hot water hydronic distribution.
Metro Therm | Microbooster Pump | Website | Heat Pump | DHW | Heat Pump | Ultra Low Temperature District Heating or Low-temp heat recovery | Micro-booster Heat Pump (MbHP) | Residential | Small Residential Heating Solution. Boost DHW to set-point temperatures where district heating supply temperature is insufficient for HW production. i.e. Ultra Low temperature District Heating (ULTDH)
Darcy |  | website | Heat Pump | Heating, Cooling | Groud Source Heat Pump |  | Ground Source Heat pump | All | Outside of scope - ground source heat pump. Enhanced drilling and Ground heat exchanger technology that increases performance with fewer boreholes
Aermec | NRP, NXW, ANK, etc | website | Heat Pump | Heating, Cooling, DHW |  |  |  | All | Aermec carries a range of large capacity heat pump products for commercial HVAC and DHW plants, as well as terminal units, etc.
PHNIX | PASHW | website | Heat Pump | Heating, Cooling, DHW |  |  |  | All | Large capacity air to water hp
Swegon | Range of products | website | Heat Pump | Heating, Cooling |  |  |  | All | Range of large capacity air source and water source heat pumps
Carrier | WeatherMaker | website | Heat Pump | Heating, Cooling |  |  |  | Commercial | Large capacity air to air hp. Carrier also offer a range of VRF products.
Mitsubishi | City Multi | website | Heat Pump | Heating, Cooling |  |  |  | All | Range of air soure and water source VRF products with larger capacities for commercial applications
ClimateMaster | Range of products | website | Heat Pump | Heating, Cooling, Ventilation |  |  |  | All | Range of water soure and air source products for a variety of commercial & multi-family applications
Ice Air | Range of products | website | Heat Pump | Heating, Cooling, DHW |  |  |  | All | NY manufacturer of a range products for commercial and multi-family HVAC and DHW applications.
Colmac | CxV, CxA, CxW | website | Heat Pump | DHW |  |  |  | Commercial | Larger scale heat pump water heaters. CxV operates at low ambient temp.
Mayekawa | Unimo | website | Heat Pump | DHW, Heating |  |  |  | All | Larger scale CO2 air and/or water source heat pump water heater. Mayekawa specializes in high temp heat pumps. E.g. They also have an ammonia heat pump for high temp hot water.
Itomic | Ecocute | website | Heat Pump | DHW |  |  |  | All | Large scale CO2 heat pump water heater
Mitsubishi Heavy Industry | HPWHs | website | Heat Pump | DHW |  |  |  | All | Large scale heat pump water heaters
AO Smith | CHP-120 | website | Heat Pump | DHW |  |  |  | All | Larger scale air source heat pump water heaters
Nyle | Range of products | website | Heat Pump | DHW |  |  |  | All | Range of larger scale heat pump water heaters
Water furnace | Range of products | website | Heat Pump | Heating, Cooling, Ventilation |  |  |  | All | Variety of large scale geo, water source and air handler products
Viking Heat Engines | HeatBooster | website | Heat Pump | DHW, Heating |  |  |  | All | High temp heat pump booster
Emerson Climate Technologies | NeatPump | website | Heat Pump | DHW, Heating |  |  |  | All | High temp ammonia heat pump
Friedrich | VRP | website | Heat Pump | Heating, Cooling |  |  |  | Residential | Residential scale plug & play product delivers variable-speed cooling, low ambient heating and make-up air
Build Equinox | CERV | website | Heat Pump | Heating, Cooling, Ventilation | Heat Pump ERV |  |  | Residential | ERV with integral heat pump, smart controls, IAQ monitoring, variable speed, recirc mode, web-connected
Treau |  | website | Heat Pump | Heating, Cooling |  |  |  | Residential | Early-stage startup with an over-the-window-sill, DIY, plug-in heat pump in Beta testing
Chiltrix |  | website | Heat Pump | Heating, Cooling, DHW |  |  |  | Residential | Residential scale air source heat pump
Mini-split manufacturers with low ambient functionality: Mitsubishi, Fujitsu, LG, Gree, Daikin, Arctic Heat Pumps, Chiltrix | [7 empty] | Residential
Residential heat pump water heater manufacturers: Sanden (CO2), Rheem, Bradford White, AO Smith, Steilbel Eltron | [7 empty] | Residential
NY manufacturers of multi-family heat pump products (PTHPs, WSHPs, etc): Islandaire, EMI RetroAir, Cold Point Corp Adirondack Aire | [7 empty] | Residential
Residential air to water heat pump manufacturers with low ambient functionality: SpacePack Hydronics (Solstice Extreme), Daikin, Gree | [7 empty] | Residential
WSHP manufacturers: ClimateMaster, Bulldog, Ice Air… | [7 empty] | Residential
Oilon | ChillHeat | website | Heat Pump | Heating, Cooling, DHW |  |  |  | All | Industrial hydronic heat pumps and chillers. The ChillHeat product family consist of three product series: - P-​series products: up to 120°C capable high temperature - S-​series products: high capacity - RE-series products: ground source application | [12 empty] | Finland
Water Furnace | WC Variable Speed Dual Screw Chiller | website | Heat Pump | Heating, Cooling, ERV |  |  |  | All | Water-to-water chillers with R-134a refrigerant. Can provide up to 140F hot water in heat recovery application. High efficiency compressor, smart communicating controls, remote monitoring options, and integration into building automation systems.
Enogia | ENO-10LT to 180LT | website | Power Generation | Electrical |  |  |  | All | Waste heat recovery unit to generate electricity using Organic Rankine Cycle (ORC) technology. Modules rated from 10kW to 180kW of electricity | [12 empty] | France
CO2 PEC | Net Zero Range | website | Heat Pump | Heating, Cooling, DHW |  |  |  | All | CO2 heat pumps. The Net Zero Range can heat up water in excess of 90°C whilst simultaneously producing chilled water. Simultaneous heating and cooling can bring COP up to 8, heating alone has COP around 4. | [12 empty] | UK
Note on J12: Edie Taylor: https://www.sciencedirect.com/science/article/abs/pii/S0735193313002170?via%3Dihub https://www.sciencedirect.com/science/article/abs/pii/S014070071730230X?via%3Dihub

## Data Point Descriptions
Data Point Category | Data Point | Description | Data Type | In-depth Data Type (i.e. Range Options, Dropdown Options) | Notes for data collection process | Comments from RMI | Comments from Elementa
Basic Information | Company Name | Name of company. | Text / description
| Product name | Specific product name (if different than company name) | Text / description
| Website/Reference | Link to product website or most relevant reference. | Link |  | only most relevant link (additional links can be entered in additional info columns)
| Technology Type | Specific technology type that the the product could be classified as. | Description |  | General name of category or type of technology (eg. radiant panel) | Aiming for discrete consistent terminology, may need to manually edit though given diversity of tech
| Any Critical Prerequisite Condition |  | Qualitative Description
| Basic Description | Description of the technology and how it works in 1-2 sentences. | Qualitative Description
Applicability | Technology Focus Area | What technology category this technology solution falls under | drop down | Energy Distribution, Thermal Storage, Heat Pump, Power Storage, Power Generation, Building Envelope, Financing, Other
| Relevant Building Type | What type of building this technology could be implemented in. | drop down | Commercial, Residential, All |  | (Considered additional breakdown (eg. tall vs standard height etc) however we do not want relevant tech to be filtered out une
| Building System | Broad building system that the technology would be applied to | keyword | Heating, Cooling, Heating and Cooling, DHW, Electrical |  |  | Heating, Cooling, Controls, DHW, Electrical, Energy Storage
| Subsystem Type | Specific sub system that technology is applicable to within broader building system category | keyword | Hydronic Systems, Chiller Plant, Boiler Plant, Steam radiators, Heat Rejection, Forced Air, Ice storage | Intention is to enable searching of database by specific subsystems a building currently has (eg. Steam radiators). Only use specific options where tech applies only to one specific sub system | Aiming for discrete consistent terminology, may need to manually edit though given diversity of tech | Could also classify based on: 1) Energy transfer media (i.e. CW, HHW, CHW, Steam, Electric, etc.) and 2) Associated Equipment (VRF, Heat Pumps, etc)
Building Decarbonization Attributes | Climate Impact Potential (Building Level) | Range based estimate of % GHG reduction for applicable building type (eg. 1 - 5%). Based upon current carbon factor calculations. | Range [discrete options eg. 1-5%] | 0-100% | Simple calculation / estimate. Documented in a separate spreadsheet based on end use breakdowns from several representative building models State level will be rough area weighted average by building types relative to overall building stock | For each technology / product both RMI and EE will review, additional reviewers will be leveraged as needed
| Future Climate Impact Potential (Building Level) | Range based estimate of % GHG reduction for applicable building type (eg. 1 - 5%). Based on future carbon factor calculatoins. | Range [discrete options eg. 1-5%]
| Climate Impact Potential (State Level) | Range based estimate of % GHG reduction if applied across applicable building types (i.e. weighted average by floor areas) Based upon current carbon factor calculations. | % | 0-100%
| Future Climate Impact Potential (State Level) | Range based estimate of % GHG reduction if applied across applicable building types (i.e. weighted average by floor areas). Based upon future carbon factor calculations. | %
| Climate impact type | Category for how this tech reduces emissions | Dropdown | Efficiency, Demand Flexibility, Enabler | Enabler would be something that is done primarily to enable other meaures such as a heat pump | added
| Climate Impact Description | Explaination of how this technology reduces GHG emsisions | Qualitative Description | description
| Cost Effectiveness Potential | How cost effective is this technology expected to be for typical retrofit applications? | Dropdown | [Short Term Payback, Medium Term Payback, Long Term Payback] | Short term < 3 years, Medium < 10 years, Long > 10 years. Based on manufacture claims / case studies, with some professional judgement applied, will factor in carbon reduction calculation / assessment | For each technology / product both RMI and EE will review, additional reviewers will be leveraged as needed
| Cost Effectiveness Description | What makes this technology cost effective and/or what might make it more cost effective in the coming years. | Qualitative Description |  | Key rationale / expalation of category selected above
Technology Review | Tech Development Category | Basic category of technology readiness in terms of availability | Dropdown | US Best Practice, Global Best Practice, Emerging
| Technology Readiness Level | TRL Level 1-9 | Range (discrete or N/A) | 1--9 | Definitions below. (N/A if not emerging)
| Risk Category | Risk of implementing technology | Dropdown | low, medium, high | Considering technology complexity, potential for failure, maintenance requirements. High would be a technology with many complex interative parts / subsystems using rare or hard to find materials / components
| Key Technical Risks | Qualitative description of risks for technology. | Qualitative Description |  |  | (note deleted barriers from original data point title, addressed elsewhere)
Company Data | HQ Location | Location of the company's headquarters - City, State, Country. | Text / description
| Affiliated Locations in US | Additional locations of offices in the US. - City, State, Country | Text / description
| Growth Phase | Growth Phase Category | Dropdown | Pre-startup, Start Up / launch, Growth, Large established company
| Company Size | Estimate size of the company (# of employees) at the date of research. | Dropdown | 1-10 employees, 11-50 employees, 51-200 employees, 200+ employees
| Contact Information @ Company | Email and/or Phone Number for contacted representative at the company. | Qualitative Description
Market Data | US Total Market Size (TM) | Total potential sales value ($) sales associated with implementation in all buildings the technology could be applied to in the US. We expect this metric would primarily useful for prospective technology investors and policy makers. | $ |  | ‘rough order of magnitude’ type approximation intended for comparison purposes. Based on extrapolation of product price and application to all applicable building types. | *@NYSERDA - please let us know if you have any input here. We anticipate some companies in growth phase may not be willing to share this data. We may be able to develop our own estimate but for some might need to mark as "unknown"
| US Current Market Size | Current market size is defined as the $/yr sales value associated with the technology category (annual sales of this technology + its competitors) in the US. This is the existing state of the market for each technology category.
| US Market Penetration | Market penetration in the US (otherwise known as absolute market share) is defined as the penetration of the technology relative to the current market size (i.e. relative to competing products) | %
| NYS Market Size | As per above, limited to New York State | $
| NYS Current Market Size | As per above, limited to New York State
| NYS Market Penetration | As per above, limited to New York State | %
| Global Market Size | As per above, Global | $
| Global Current Market | As per above, Global
| Global Market Penetration | As per above, Global | %
| Reason for Widespread/Limited Adoption |  | Qualitative Description
Installation Data | Relevant Trigger Points | What events would provide a good opportunity to apply this technology? | Dropdown | Full Major Building Rehabilitation, Rennovation of tenant space, Chiller or Boiler Replacement, Electrical System Upgrade |  |  | PD- MEP Infrastructure replacement or renovation in lieu of Chiller or Boiler Replacement.
Additional Info & Comments | References | Relevant papers published, case studies on technology, patent #'s …etc. | Link / text
| Additional Info | Any additional notes or important comments on the technology not captured | Description
Additional data points considered, but recommeded not to include in current database
| Installation Owner | Who would most likely own the installation of the technology in the building. | Dropdown | Tenant, Owner |  | Suggested at kickoff. There are many different ownership structures that this could change, and is specific to individual leases (net vs. gross vs. fitout terms) - don't want to get too prescriptive and exclude opportunities.
| Resultant Effects | Which areas of the building would be effected by the installation construction, and which areas would benefit from the installation? | Qualitative Description |  |  | Suggested at kickoff. This may overlap with triggers and install location
| Installation Location | Where would the technology likely be installed? | Dropdown | Perimeter vs Core |  | Suggested at kickoff. We feel this is covered sufficiently by the other categories
| Supply Chain Ownership | What aspect of the implementation of the technology does the company own? | Dropdown | Manufacturer, Distributor, Commissioning Driven |  | Suggested at kickoff. This is not easy to define for many of the technologies (some are tbd, others may have multiple), does not seem critical
| HVAC system layout type | Type of HVAC configuration that this tech is best suited for | Keyword | Central Fan Room(s), Floor-by-Floor w/ central hydronic, Floor-by-floor water-cooled dx, Distributed zonal equip |  | RMI idea to add. Recommend eliminating but include in the key prereq column if any of these are relevant to a given tech | What equipment/technology is specific to system type layouts?
Technology Readiness Levels
Level 1: Basic principles of concept are observed and reported
Scientific research begins to be translated into applied research and development. Activities might include paper studies of a technology's basic properties.
Level 2: Technology concept and/or application formulated
Invention begins. Once basic principles are observed, practical applications can be invented. Activities are limited to analytic studies.
Level 3: Analytical and experimental critical function and/or proof of concept
Active research and development is initiated. This includes analytical studies and/or laboratory studies. Activities might include components that are not yet integrated or representative.
Level 4: Component and/or validation in a laboratory environment
Basic technological components are integrated to establish that they will work together. Activities include integration of "ad hoc" hardware in the laboratory.
Level 5: Component and/or validation in a simulated environment
The basic technological components are integrated for testing in a simulated environment. Activities include laboratory integration of components.
Level 6: System/subsystem model or prototype demonstration in a simulated environment
A model or prototype that represents a near desired configuration. Activities include testing in a simulated operational environment or laboratory.
Levels 7 through 9 represent the pre-commercialization gap for innovations.
Level 7: Prototype ready for demonstration in an appropriate operational environment
Prototype at planned operational level and is ready for demonstration in an operational environment. Activities include prototype field testing.
Level 8: Actual technology completed and qualified through tests and demonstrations
Technology has been proven to work in its final form and under expected conditions. Activities include developmental testing and evaluation of whether it will meet operational requirements.
Level 9: Actual technology proven through successful deployment in an operational setting
Actual application of the technology in its final form and under real-life conditions, such as those encountered in operational tests and evaluations. Activities include using the innovation under operational conditions.

## Dropdown Options (hidden)
Relevant Building Type | Climate Impact Type | Tech Development Category | Risk Category | Growth Phase | Company Size | Relevant Trigger Points | Installation Location | Supply Chain Ownership | Cost Effectiveness Potential | Climate Impact Potential
Commercial | Efficiency | US Best Practice | Low | Pre-startup | 1-10 Employees | Full Major Building Retrofit | Tenant Space | Manufacturer | Short-term Payback | < 1 %
Residential | Demand Flexibility | Global Best Practice | Medium | Startup/Launch | 11-50 Employees | Renovation of Tenant Space | Back-of-house | Distributor | Medium-term Payback | 1 - 5%
All | Enabler | Emerging | High | Growth | 51-200 Employees | Chiller/Boiler Replacement |  | Commissioning Driven | Long-term Payback | 6 - 10%
| Efficiency & Demand Flexibility |  |  | Established | 200+ Employees | Electrical System Upgrade |  |  | Unknown | 11 - 20%
[6 empty] | No Trigger Required |  |  |  | 21 - 30%
31-40%
41-50%